

INTER-OFFICE MEMORANDUM **DATE:** 05/10/2021 **TO:** SHMILLIAM **FROM:** travis **SUBJECT:** Another Project  
 DSC Engineering Review Comments  
 DSC File: PRO-52

DSC cannot approve the project at this time. The following comments must first be addressed:  
  
1: Provide silt fence around the extents of disturbance. ((VESCH 7.12).)  
2: Establish plz. ((DEQ Spec. No. 7.).)  
3: The shown permeable pavement system is setback less than 5' from the adjacent building. Relocate the system away from the building to meet the required setback. ((DEQ Spec. No. 7. Table 7.4).)